## Method
Method: indicative rooftop solar sizing, generation, savings, payback and CO2 for 20 Oxford sites
OZ. Prepared 9 October 2026; checked by Zara Pashov, 10 October 2026. Workbook sheets: Method (this sheet), Inputs (every number and its source), Results (one row per site), Calculations (every step, every scenario).
1. Purpose and status
To give an installer an indicative, desktop-derived estimate of system size, year-1 generation, annual saving, simple payback and CO2 avoided for 20 commercial roofs in Oxford City. These are not quotes. No site visit, meter data, structural check or grid-connection check has been made.
2. How the 20 sites were chosen (summary)
Buildings were ranked with the OZ scorecard v0.3 (roof footprint area and site gap), the method that won the OZ arena run on 2 October 2026, using OpenStreetMap building outlines for Oxford City (local authority E07000178). Buildings with solar already mapped in OpenStreetMap, and sites with their own rooftop solar record in the Renewable Energy Planning Database, were removed. Zara Pashov checked the top 50 sites and 16 further large roofs on satellite imagery on 7 October 2026 and chose these 20: no panels visible, roof judged usable, occupier identified, a mix of sectors.
3. Decisions taken (Zara Pashov, 9 October 2026)
a) Roof area: main building only (the one checked on satellite). Four sites have more buildings; these are not included.
b) Sizing: roof-limited, i.e. what the usable roof can physically hold. Results above 1 MWp are flagged as likely limited by site demand or grid capacity.
c) Self-consumption: the same three scenario values for every site (40% / 60% / 80%); no published source gives this by sector.
d) Carbon: UK grid-average factor (DESNZ conversion factors), as businesses use for their own carbon reporting.
e) Costs: published commercial price range for capital cost; official DECC 2015 running costs; DESNZ average business electricity price; business export tariffs from Ofgem's Smart Export Guarantee report.
f) Unipart Logistics Cowley: roof area shown, sizing pending, because its roofs are angled and the planes have not been measured. The coverage values used here come from studies of flat roofs.
g) Sainsbury's: roof area is Zara's measurement on satellite imagery (5,488 m²), not the OpenStreetMap outline (8,401 m²).
4. Calculation, step by step (symbols as on the Inputs sheet)
Step 1. Roof area A (m²): OpenStreetMap footprint of the main building (plan area). For flat roofs, plan area and roof area are the same.
Step 2. System size (kWp) = A × f × rho ÷ 1,000, where f is the share of roof covered by panels and rho is the module power density in W per m² of module.
Step 3. Generation (kWh/yr) = system size × Y, where Y is the PVGIS specific yield for Oxford (kWh per kWp per year).
Step 4. Used on site (kWh/yr) = generation × s; exported (kWh/yr) = generation × (1 − s), where s is the self-consumption share.
Step 5. Gross saving (£/yr) = (used on site × p_imp + exported × p_exp) ÷ 100, with prices in pence per kWh.
Step 6. O&M cost (£/yr) = system size × o. Net saving (£/yr) = gross saving − O&M cost.
Step 7. Capital cost (£) = system size × c. Simple payback (years) = capital cost ÷ net saving.
Step 8. CO2e avoided (t/yr) = generation × g ÷ 1,000, where g is the grid-average carbon factor. It is applied to all generation, used or exported, since both displace grid electricity at the grid-average rate.
5. Scenarios
Each scenario sets every input to the same side, so Low is pessimistic on all of them and High optimistic on all of them: Low = least roof covered (29.4%), least self-use (40%), lowest export price (3.0 p), highest capital cost (£1,100/kWp), highest running cost (£11.4/kW/yr). Central = 40%, 60%, 4.1 p, £900, £9.5. High = 46.2%, 80%, 4.1 p, £700, £7.6. The electricity price (24.51 p), yield (922.3 kWh/kWp), power density (230 W/m²) and carbon factor are the same in all three.
Because every input except roof area is the same for all sites, payback is identical across sites within a scenario. Size, generation, savings and CO2 scale with roof area. Site-specific payback needs site data, above all each site's daytime demand.
6. Limitations
1. Roof area comes from OpenStreetMap outlines (plan area), which can include canopies or adjoining structures, as at Sainsbury's. Roof condition, structural capacity, rooflights, plant and shading were judged only by eye on satellite imagery.
2. The coverage shares come from European and US studies of flat roofs (Bódis et al. 2019; Kakoulaki et al. 2026; Gagnon et al. 2016), not from UK surveys of these buildings. They assume south-facing racks at 15–20°, while the yield uses a 10° tilt.
3. Self-consumption is an assumption, not data. It is the largest single driver of savings and payback.
4. The electricity price is the all-business average for Q2 2026. Larger consumers pay less per kWh, and it has not been confirmed whether the average includes fixed charges that solar does not avoid. Prices change every quarter.
5. The capital cost range is a trade source, and running costs are 2014 prices, not inflated. No official cost figure for commercial rooftop PV newer than 2015 was found.
6. Results are for year 1: no degradation (median 0.5%/yr, Jordan and Kurtz 2013), price changes, financing, tax allowances, inverter replacement timing or discounting. Simple payback is not a full investment appraisal.
7. Business rates: rooftop solar in England is exempt from business rates from 1 April 2022 to 31 March 2035 (SI 2022/405, Explanatory Memorandum), so no rates cost is included.
8. Systems are sized to the roof, not to demand or grid capacity. Large systems may need a grid application and may be limited by the local network.
7. Still to confirm before sharing
a) Specific yield. Open the PVGIS web tool (re.jrc.ec.europa.eu/pvg_tools), choose Grid-connected PV, enter latitude 51.7514, longitude −1.2407, installed peak power 1 kWp, system loss 14%, slope 10°, azimuth 0°. Note the yearly energy E_y and the radiation database shown, then type E_y into Inputs C7:E7. The figure now used (922.3) came from the PVGIS v5.2 API during the arena run; the current web tool runs version 5.3 (PVGIS-SARAH3), so the value may differ slightly.
b) Electricity prices by consumer size band (DESNZ table 3.4.2), if a size-specific price is wanted. Only the all-business average could be confirmed from an official source here.
8. References (Harvard)
Bódis, K., Kougias, I., Jäger-Waldau, A., Taylor, N. and Szabó, S. (2019) 'A high-resolution geospatial assessment of the rooftop solar photovoltaic potential in the European Union', Renewable and Sustainable Energy Reviews, 114, 109309. Available at: https://fenix.ciencias.ulisboa.pt/downloadFile/1126037345801908/Bodis-2019-A-high-resolution-geospatial-assess.pdf [Accessed on: 09/10/2026].
DESNZ (2026a) Quarterly Energy Prices: September 2026. London: Department for Energy Security and Net Zero. Available at: https://assets.publishing.service.gov.uk/media/6aba2810fe72ed1e2b02f0e7/Quarterly_Energy_Prices_September_2026.pdf [Accessed on: 09/10/2026].
DESNZ (2026b) 2026 Government greenhouse gas conversion factors for company reporting: methodology report. London: Department for Energy Security and Net Zero. Available at: https://assets.publishing.service.gov.uk/media/6a2940543b15d05a7ce3202e/2026-GHG-conversion-factors-methodology-report.pdf [Accessed on: 09/10/2026].
European Commission Joint Research Centre (n.d.) PVGIS user manual. Available at: https://joint-research-centre.ec.europa.eu/photovoltaic-geographical-information-system-pvgis/getting-started-pvgis/pvgis-user-manual_en [Accessed on: 09/10/2026].
European Commission Joint Research Centre (2026) PVGIS 5.2 API, PVcalc, lat 51.7514, lon −1.2407, peakpower 1, loss 14, angle 10, aspect 0. Retrieved 02/10/2026 during the OZ arena run (to be re-confirmed, section 7).
Gagnon, P., Margolis, R., Melius, J., Phillips, C. and Elmore, R. (2016) Rooftop Solar Photovoltaic Technical Potential in the United States: A Detailed Assessment. NREL/TP-6A20-65298. Golden, CO: National Renewable Energy Laboratory. Available at: https://nrel.gov/docs/fy16osti/65298.pdf [Accessed on: 09/10/2026].
Jinko Solar (2024) Tiger Neo JKM435-460N-54HL4R-(V) datasheet. Available at: https://www.jinkosolar.com/uploads/JKM435-460N-54HL4R-(V)-F8-EN.pdf [Accessed on: 09/10/2026].
Joju Solar (2026) Commercial rooftop solar. Available at: https://www.jojusolar.co.uk/for-business/commercial-rooftop/ [Accessed on: 09/10/2026].
Jordan, D.C. and Kurtz, S.R. (2013) 'Photovoltaic degradation rates: an analytical review', Progress in Photovoltaics: Research and Applications, 21(1), pp. 12–29. Available at: https://www.osti.gov/biblio/1045052 [Accessed on: 09/10/2026].
Kakoulaki, G., Kenny, R., Taylor, N., Gracia-Amillo, A.M., Szabo, S., Martínez, A.M., Thiel, C. and Jäger-Waldau, A. (2026) 'Mapping Europe's rooftop photovoltaic potential with a building-level database', Nature Energy, 11(2), pp. 324–333. Available at: https://www.nature.com/articles/s41560-025-01947-x [Accessed on: 09/10/2026].
LONGi (2025) LR7-54HVH 480-500 M datasheet (draft, 08/04/2025). Available at: https://static.longi.com/LR_7_54_HVH_480_500_M_BGV_01_20250408_BGV_02_568afe65cb.pdf [Accessed on: 09/10/2026].
Ofgem (2025) Smart Export Guarantee Annual Report: Year 5 (April 2024 – March 2025). London: Ofgem. Available at: https://www.ofgem.gov.uk/sites/default/files/2025-12/Smart_Export_Guarantee_Annual_Report_Year_5-20251203191140.pdf [Accessed on: 09/10/2026].
OpenStreetMap contributors (2026) Oxfordshire extract, downloaded 02/10/2026. Licensed under the Open Database Licence (ODbL).
Parsons Brinckerhoff (2015) Small-Scale Generation Costs Update. Report for the Department of Energy and Climate Change. Available at: https://assets.publishing.service.gov.uk/government/uploads/system/uploads/attachment_data/file/456187/DECC_Small-Scale_Generation_Costs_Update_FINAL.PDF [Accessed on: 09/10/2026].
The Valuation for Rating (Plant and Machinery) (England) (Amendment) Regulations 2022 (SI 2022/405), Explanatory Memorandum. Available at: https://www.legislation.gov.uk/uksi/2022/405/pdfs/uksiem_20220405_en.pdf [Accessed on: 09/10/2026].
Trina Solar (2025) Vertex N TSM-NEG19RC.20 datasheet. Available at: https://static.trinasolar.com/sites/default/files/DT-M-0045_Datasheet_Vertex_NEG19RC.20_EN_2025_B.pdf [Accessed on: 09/10/2026].
Attribution: contains OpenStreetMap data © OpenStreetMap contributors, available under the Open Database Licence. Contains public sector information licensed under the Open Government Licence v3.0.

## Inputs
Inputs: every number the calculation uses, with its source
Blue text = a typed input. Black = a formula. Yellow fill = an assumption or a value still to be confirmed. Change any blue cell and every result in the workbook updates.
Parameter | Symbol | Low | Central | High | Unit | Source (see Method, section 8) | Exact quote from the source, or how the value was derived | Status
Share of roof area covered by panels (module area / roof area) | f | 0.294 | 0.4 | 0.462 | fraction | Low: Bódis et al. (2019). Central: Kakoulaki et al. (2026). High: Gagnon et al. (2016). | Low: "approximately half (49–64%) of EU roofs appeared to be suitable for PV" and "an additional reduction coefficient (60%) has been applied to estimate the net area"; lower bound 0.49 × 0.60. Central: for non-residential buildings "the PV installations were set at 40% of the total rooftop area"; "Spacing between modules and module racks is taken into account in the 25% or 40% installation fraction". High: "49% suitable for medium buildings and 66% for large buildings" and "For flat roofs, the ratio of module area to roof area was assumed to be 0.7"; 0.66 × 0.70. | VERIFIED (quotes opened 09/10/2026)
Module power density | rho | 230 | 230 | 230 | W per m² of module | Median of three current module datasheets (rows 21-23), rounded to the nearest 10 W/m². | Derived: rated power ÷ module area for each datasheet; midpoint of each product's range; median of the three. | VERIFIED datasheets; median is derived
Specific yield (annual generation per kWp) | Y | 922.3 | 922.3 | 922.3 | kWh per kWp per year | PVGIS v5.2 API, EC Joint Research Centre. Retrieved 02/10/2026 during the OZ arena run. | Settings: lat 51.7514, lon −1.2407 (mean location of the 1,790 Oxford City buildings), peak power 1 kWp, system loss 14% (PVGIS default: "We have given a default value of 14% for the overall losses"), tilt 10°, azimuth 0° (south). Output E_y = 922.3. | TO CONFIRM: re-run in the PVGIS web tool (Method, section 7)
Self-consumption (share of generation used on site) | s | 40% | 60% | 80% | fraction | Assumption chosen by Zara Pashov, 09/10/2026. | No published source gives self-consumption by sector. Systems here are sized to the roof, not to site demand, so very high self-use is less likely. To be tested with installers. | ASSUMPTION
Electricity price avoided by self-consumption | p_imp | 24.51 | 24.51 | 24.51 | p per kWh | DESNZ (2026a) Quarterly Energy Prices, September 2026, p. 8. | "In quarter 2 2026, the average electricity price including CCL was 24.51 pence per kWh". All-business average; prices differ by size band. The quoted text does not state the VAT treatment. | VERIFIED (all-business average)
Export price for electricity not used on site | p_exp | 3 | 4.1 | 4.1 | p per kWh | Ofgem (2025) Smart Export Guarantee Annual Report, Year 5 (Apr 2024 – Mar 2025), Figures 2.1–2.3. | Untied business export tariffs named in the report: EDF Variable Business 3 p/kWh (low); Octopus Business 4.1 p/kWh (central and high). These are 2024-25 offers. | VERIFIED (2024-25 tariffs)
Capital cost (installed) | c | 1100 | 900 | 700 | £ per kWp | Joju Solar (2026) Commercial rooftop solar (trade source). | "the average cost of a commercial rooftop solar installation in the UK is between £700 and £1,100 per kilowatt peak (kWp), with larger installations typically costing less per kWp". Central = midpoint. Joju attributes the figure to the Solar Trade Association; VAT not stated. No official figure newer than 2015 was found. | VERIFIED wording; trade source
Operation and maintenance cost | o | 11.4 | 9.5 | 7.6 | £ per kW per year (2014 prices) | Parsons Brinckerhoff for DECC (2015) Small-Scale Generation Costs Update, section 2.2.4.8. | Band 250–5,000 kW: low 7.6, central 9.5, high 11.4 £/kW/yr. Opex "should include labour, planned maintenance and lifecycle replacement costs". The pessimistic (Low) scenario uses the high cost. 2014 prices, not inflated. | VERIFIED; dated (2014 prices)
Carbon factor for UK grid electricity | g | 0.13096 | 0.13096 | 0.13096 | kg CO2e per kWh | DESNZ (2026b) 2026 GHG conversion factors methodology report, Table 9, p. 36. | Row "2025", electricity GENERATED, total = 0.13096 kg CO2e/kWh (UK grid average, 2025 data). Transmission and distribution losses (0.01299) are not added. | VERIFIED
Annual degradation of panel output (not applied) | d | 0.5% | 0.5% | 0.5% | per year | Jordan and Kurtz (2013). | "Nearly 2000 degradation rates… showing a median value of 0.5%/year." Not applied: all results are year 1. | VERIFIED; documented only
Flag systems larger than | flag | 1000 | 1000 | 1000 | kWp | Decision by Zara Pashov, 09/10/2026. | Systems are sized to the roof. Above 1 MWp they are flagged as likely limited by site demand or grid capacity. | DECISION
Module datasheets used for the power density (row 6)
Module (datasheet) | Rated power, min (W) | Rated power, max (W) | Length (mm) | Width (mm) | W per m², min | W per m², max | Midpoint W per m² | Source URL
LONGi LR7-54HVH 480-500 M (datasheet dated 08/04/2025, marked draft) | 480 | 500 | 1800 | 1134 | 235.1558 | 244.9539 | 240.0549 | https://static.longi.com/LR_7_54_HVH_480_500_M_BGV_01_20250408_BGV_02_568afe65cb.pdf
Jinko Tiger Neo JKM435-460N-54HL4R-(V) (2024) | 435 | 460 | 1762 | 1134 | 217.7059 | 230.2178 | 223.9619 | https://www.jinkosolar.com/uploads/JKM435-460N-54HL4R-(V)-F8-EN.pdf
Trina Vertex N TSM-NEG19RC.20 (2025) | 610 | 635 | 2382 | 1134 | 225.8266 | 235.0817 | 230.4542 | https://static.trinasolar.com/sites/default/files/DT-M-0045_Datasheet_Vertex_NEG19RC.20_EN_2025_B.pdf
[6 empty] | Median of midpoints | 230.4542

## Results
Oxford City: indicative rooftop solar sizing, generation, savings, payback and CO2 for 20 checked sites
Checked by Zara Pashov, 10 October 2026. Indicative desktop estimates from public data, not quotes. Low / Central / High are bundled scenarios (see Method). Figures are for year 1. Inputs and sources: Inputs sheet.
Rank (check sheet) | Site | Found in tab | OSM building type | Buildings on site | OSM footprint, main building (m²) | Roof area used (m²) | Roof area source | Sizing status | Satellite check (Zara, 7 Oct 2026) | System size (kWp) |  |  | Generation (MWh/yr) |  |  | Net saving (£/yr) |  |  | Simple payback (years) |  |  | CO2e avoided (t/yr) |  |  | Flag | Satellite view
[10 empty] | Low | Central | High | Low | Central | High | Low | Central | High | Low | Central | High | Low | Central | High
1 | Unipart | Top 50 | industrial | 1 | 9774 | 9774 | OpenStreetMap building outline (main building only) | Sized | No panels visible; roof usable: Yes | 660.9179 | 899.208 | 1038.5852 | 609.5646 | 829.3395 | 957.8872 | 63199.4078 | 127021.3649 | 187783.9426 | 11.5034 | 6.3713 | 3.8715 | 79.8286 | 108.6103 | 125.4449 | High scenario above 1 MWp: check site demand and grid capacity | Satellite
11 | Unipart Logistics Cowley | Top 50 | warehouse_logistics | 1 | 80278 | 80278 | OpenStreetMap building outline (main building only) | Pending | No panels visible; roof usable: Yes. Note: roofs angled might not be great for solar, array probs smaller than anticipated | [15 empty] | Sizing pending: angled roof, roof planes not measured (LiDAR or survey needed) | Satellite
12 | Sainsbury's | Top 50 | retail | 1 | 8401 | 5488 | Zara Pashov, measured on satellite imagery, 7 Oct 2026 (OSM outline 8,401 m² judged too large) | Sized | No panels visible; roof usable: Yes. Note: I think the roof size is smaller than this estimate, I estimate 5488m2 | 371.0986 | 504.896 | 583.1549 | 342.2642 | 465.6656 | 537.8437 | 35485.8144 | 71321.1838 | 105438.7433 | 11.5034 | 6.3713 | 3.8715 | 44.8229 | 60.9836 | 70.436 |  | Satellite
50 | Ozone Leisure Centre | Top 50 | retail | 1 | 11652 | 11652 | OpenStreetMap building outline (main building only) | Sized | No panels visible; roof usable: Yes | 787.9082 | 1071.984 | 1238.1415 | 726.6878 | 988.6908 | 1141.9379 | 75342.6949 | 151427.5572 | 223865.2035 | 11.5034 | 6.3713 | 3.8715 | 95.167 | 129.479 | 149.5482 | Central size above 1 MWp: likely limited by site demand or grid capacity | Satellite
26 | Kassam Stadium | Top 50 | hospitality_leisure | 3 | 5428 | 5428 | OpenStreetMap building outline (main building only) | Sized | No panels visible; roof usable: Yes | 367.0414 | 499.376 | 576.7793 | 338.5222 | 460.5745 | 531.9635 | 35097.85 | 70541.4333 | 104285.9874 | 11.5034 | 6.3713 | 3.8715 | 44.3329 | 60.3168 | 69.6659 |  | Satellite
13 | Holiday Inn | Top 50 | untagged_large_no_zone | 1 | 4424 | 4424 | OpenStreetMap building outline (main building only) | Sized | No panels visible; roof usable: Yes | 299.1509 | 407.008 | 470.0942 | 275.9069 | 375.3835 | 433.5679 | 28605.9116 | 57493.6074 | 84996.538 | 11.5034 | 6.3713 | 3.8715 | 36.1328 | 49.1602 | 56.7801 |  | Satellite
24 | The Oxford Academy | Top 50 | education | 3 | 9070 | 9070 | OpenStreetMap building outline (main building only) | Sized | No panels visible; roof usable: Yes | 613.3134 | 834.44 | 963.7782 | 565.6589 | 769.604 | 888.8926 | 58647.2917 | 117872.2918 | 174258.2729 | 11.5034 | 6.3713 | 3.8715 | 74.0787 | 100.7873 | 116.4094 |  | Satellite
28 | Oxford Telephone Exchange | Top 50 | untagged_in_commercial_zone | 1 | 3900 | 3900 | OpenStreetMap building outline (main building only) | Sized | No panels visible; roof usable: Yes | 263.718 | 358.8 | 414.414 | 243.2271 | 330.9212 | 382.214 | 25217.6888 | 50683.7859 | 74929.1361 | 11.5034 | 6.3713 | 3.8715 | 31.853 | 43.3374 | 50.0547 |  | Satellite
5 | Oxford Business Park (OxBio Hub) | Top 50 | untagged_in_commercial_zone | 1 | 3243 | 3243 | OpenStreetMap building outline (main building only) | Sized | No panels visible; roof usable: Yes | 219.2917 | 298.356 | 344.6012 | 202.2527 | 275.1737 | 317.8257 | 20969.4782 | 42145.5173 | 62306.4586 | 11.5034 | 6.3713 | 3.8715 | 26.487 | 36.0368 | 41.6224 |  | Satellite
7 | Oxford Business Park (John Wiley & Sons) | Top 50 | commercial_office | 1 | 2784 | 2784 | OpenStreetMap building outline (main building only) | Sized | No panels visible; roof usable: Yes | 188.2541 | 256.128 | 295.8278 | 173.6267 | 236.2269 | 272.842 | 18001.5502 | 36180.4256 | 53487.8756 | 11.5034 | 6.3713 | 3.8715 | 22.7382 | 30.9363 | 35.7314 |  | Satellite
21 | Wickes | Top 50 | retail | 1 | 2613 | 2613 | OpenStreetMap building outline (main building only) | Sized | No panels visible; roof usable: Yes | 176.6911 | 240.396 | 277.6574 | 162.9622 | 221.7172 | 256.0834 | 16895.8515 | 33958.1365 | 50202.5212 | 11.5034 | 6.3713 | 3.8715 | 21.3415 | 29.0361 | 33.5367 |  | Satellite
30 | Storage King Oxford - Self Storage Units | Top 50 | warehouse_logistics | 1 | 3558 | 3558 | OpenStreetMap building outline (main building only) | Sized | No panels visible; roof usable: Yes. Note: no name given, but it is logisitcs | 240.592 | 327.336 | 378.0731 | 221.898 | 301.902 | 348.6968 | 23006.2915 | 46239.2077 | 68358.4272 | 11.5034 | 6.3713 | 3.8715 | 29.0598 | 39.5371 | 45.6653 |  | Satellite
44 | Nuffield Trade and Industrial Park (Royal Mail East Oxford Delivery Office) | Top 50 | untagged_in_industrial_zone | 1 | 1897 | 1897 | OpenStreetMap building outline (main building only) | Sized | No panels visible; roof usable: Yes | 128.2751 | 174.524 | 201.5752 | 118.3082 | 160.9635 | 185.9128 | 12266.1425 | 24653.1133 | 36446.3003 | 11.5034 | 6.3713 | 3.8715 | 15.4936 | 21.0798 | 24.3471 |  | Satellite
39 | Unicol Engineering | Top 50 | commercial_office | 1 | 1652 | 1652 | OpenStreetMap building outline (main building only) | Sized | No panels visible; roof usable: Yes | 111.7082 | 151.984 | 175.5415 | 103.0285 | 140.1748 | 161.9019 | 10681.9543 | 21469.1319 | 31739.2135 | 11.5034 | 6.3713 | 3.8715 | 13.4926 | 18.3573 | 21.2027 |  | Satellite
40 | Magdalen Centre (Sherrington Buidling) | Top 50 | commercial_office | 1 | 2351 | 2351 | OpenStreetMap building outline (main building only) | Sized | No panels visible; roof usable: Yes | 158.9746 | 216.292 | 249.8173 | 146.6223 | 199.4861 | 230.4065 | 15201.7401 | 30553.2258 | 45168.8202 | 11.5034 | 6.3713 | 3.8715 | 19.2017 | 26.1247 | 30.174 |  | Satellite
22 | Sandhills Community Primary School | Top 50 | education | 1 | 2542 | 2542 | OpenStreetMap building outline (main building only) | Sized | No panels visible; roof usable: Yes | 171.89 | 233.864 | 270.1129 | 158.5342 | 215.6928 | 249.1251 | 16436.7602 | 33035.4317 | 48838.4267 | 11.5034 | 6.3713 | 3.8715 | 20.7616 | 28.2471 | 32.6254 |  | Satellite
99 | Oxford Retail Park (TESCO SUPERSTORE) | Large roofs | retail | 1 | 6954 | 6954 | OpenStreetMap building outline (main building only) | Sized | No panels visible; roof usable: Yes | 470.2295 | 639.768 | 738.932 | 433.6926 | 590.058 | 681.517 | 44965.079 | 90373.089 | 133604.4134 | 11.5034 | 6.3713 | 3.8715 | 56.7964 | 77.274 | 89.2515 |  | Satellite
103 | Oxford University Press | Large roofs | commercial_office | 7 | 4584 | 4584 | OpenStreetMap building outline (main building only) | Sized | No panels visible; roof usable: Yes | 309.9701 | 421.728 | 487.0958 | 285.8854 | 388.9597 | 449.2485 | 29640.4835 | 59572.9422 | 88070.5538 | 11.5034 | 6.3713 | 3.8715 | 37.4396 | 50.9382 | 58.8336 |  | Satellite
61 | Leonardo Royal Hotel Oxford | Large roofs | hospitality_leisure | 2 | 7218 | 7218 | OpenStreetMap building outline (main building only) | Sized | No panels visible; roof usable: Yes | 488.0812 | 664.056 | 766.9847 | 450.1573 | 612.4588 | 707.39 | 46672.1225 | 93803.9914 | 138676.5396 | 11.5034 | 6.3713 | 3.8715 | 58.9526 | 80.2076 | 92.6398 |  | Satellite
52 | The Manor Hospital | Large roofs | health | 1 | 4354 | 4354 | OpenStreetMap building outline (main building only) | Sized | No panels visible; roof usable: Yes | 294.4175 | 400.568 | 462.656 | 271.5412 | 369.4439 | 426.7077 | 28153.2864 | 56583.8984 | 83651.656 | 11.5034 | 6.3713 | 3.8715 | 35.561 | 48.3824 | 55.8816 |  | Satellite
| Total, sized sites |  |  |  |  | 93486 |  |  |  | 6321.5233 | 8600.712 | 9933.8224 | 5830.341 | 7932.4367 | 9161.9644 | 604487.3989 | 1214929.3353 | 1796109.0301 |  |  |  | 763.5415 | 1038.8319 | 1199.8509
Why payback is the same at every site within a scenario: every input except roof area is the same for all sites (one yield, one self-consumption share, one price, one cost per kWp), and payback does not depend on roof area. Site-specific payback needs site data, above all how much of the solar each site would use itself.

## Calculations
Calculations: every step for every site and scenario (formulas only; inputs come from the Inputs sheet)
Scenario 1 = Low (pessimistic on every input), 2 = Central, 3 = High (optimistic on every input). Each input is picked from the Inputs sheet with INDEX(row, scenario number).
Rank | Site | Scenario | Scenario no. | Sizing status | Roof area used (m²) | Panel cover share f | Power density rho (W/m²) | System size (kWp) | Specific yield Y (kWh/kWp/yr) | Generation (kWh/yr) | Self-consumption s | Used on site (kWh/yr) | Exported (kWh/yr) | Import price (p/kWh) | Export price (p/kWh) | Gross saving (£/yr) | O&M rate (£/kW/yr) | O&M cost (£/yr) | Net saving (£/yr) | Capital cost rate (£/kWp) | Capital cost (£) | Simple payback (years) | Carbon factor (kg CO2e/kWh) | CO2e avoided (t/yr)
1 | Unipart | Low | 1 | Sized | 9774 | 0.294 | 230 | 660.9179 | 922.3 | 609564.5607 | 40% | 243825.8243 | 365738.7364 | 24.51 | 3 | 70733.8716 | 11.4 | 7534.4638 | 63199.4078 | 1100 | 727009.668 | 11.5034 | 0.13096 | 79.8286
1 | Unipart | Central | 2 | Sized | 9774 | 0.4 | 230 | 899.208 | 922.3 | 829339.5384 | 60% | 497603.723 | 331735.8154 | 24.51 | 4.1 | 135563.8409 | 9.5 | 8542.476 | 127021.3649 | 900 | 809287.2 | 6.3713 | 0.13096 | 108.6103
1 | Unipart | High | 3 | Sized | 9774 | 0.462 | 230 | 1038.5852 | 922.3 | 957887.1669 | 80% | 766309.7335 | 191577.4334 | 24.51 | 4.1 | 195677.1904 | 7.6 | 7893.2478 | 187783.9426 | 700 | 727009.668 | 3.8715 | 0.13096 | 125.4449
11 | Unipart Logistics Cowley | Low | 1 | Pending | 80278 | 0.294 | 230 |  | 922.3 |  | 40% |  |  | 24.51 | 3 |  | 11.4 |  |  | 1100 |  |  | 0.13096
11 | Unipart Logistics Cowley | Central | 2 | Pending | 80278 | 0.4 | 230 |  | 922.3 |  | 60% |  |  | 24.51 | 4.1 |  | 9.5 |  |  | 900 |  |  | 0.13096
11 | Unipart Logistics Cowley | High | 3 | Pending | 80278 | 0.462 | 230 |  | 922.3 |  | 80% |  |  | 24.51 | 4.1 |  | 7.6 |  |  | 700 |  |  | 0.13096
12 | Sainsbury's | Low | 1 | Sized | 5488 | 0.294 | 230 | 371.0986 | 922.3 | 342264.2019 | 40% | 136905.6808 | 205358.5211 | 24.51 | 3 | 39716.338 | 11.4 | 4230.5236 | 35485.8144 | 1100 | 408208.416 | 11.5034 | 0.13096 | 44.8229
12 | Sainsbury's | Central | 2 | Sized | 5488 | 0.4 | 230 | 504.896 | 922.3 | 465665.5808 | 60% | 279399.3485 | 186266.2323 | 24.51 | 4.1 | 76117.6958 | 9.5 | 4796.512 | 71321.1838 | 900 | 454406.4 | 6.3713 | 0.13096 | 60.9836
12 | Sainsbury's | High | 3 | Sized | 5488 | 0.462 | 230 | 583.1549 | 922.3 | 537843.7458 | 80% | 430274.9967 | 107568.7492 | 24.51 | 4.1 | 109870.7204 | 7.6 | 4431.9771 | 105438.7433 | 700 | 408208.416 | 3.8715 | 0.13096 | 70.436
50 | Ozone Leisure Centre | Low | 1 | Sized | 11652 | 0.294 | 230 | 787.9082 | 922.3 | 726687.7698 | 40% | 290675.1079 | 436012.6619 | 24.51 | 3 | 84324.8488 | 11.4 | 8982.1539 | 75342.6949 | 1100 | 866699.064 | 11.5034 | 0.13096 | 95.167
50 | Ozone Leisure Centre | Central | 2 | Sized | 11652 | 0.4 | 230 | 1071.984 | 922.3 | 988690.8432 | 60% | 593214.5059 | 395476.3373 | 24.51 | 4.1 | 161611.4052 | 9.5 | 10183.848 | 151427.5572 | 900 | 964785.6 | 6.3713 | 0.13096 | 129.479
50 | Ozone Leisure Centre | High | 3 | Sized | 11652 | 0.462 | 230 | 1238.1415 | 922.3 | 1141937.9239 | 80% | 913550.3391 | 228387.5848 | 24.51 | 4.1 | 233275.0791 | 7.6 | 9409.8756 | 223865.2035 | 700 | 866699.064 | 3.8715 | 0.13096 | 149.5482
26 | Kassam Stadium | Low | 1 | Sized | 5428 | 0.294 | 230 | 367.0414 | 922.3 | 338522.2463 | 40% | 135408.8985 | 203113.3478 | 24.51 | 3 | 39282.1215 | 11.4 | 4184.2715 | 35097.85 | 1100 | 403745.496 | 11.5034 | 0.13096 | 44.3329
26 | Kassam Stadium | Central | 2 | Sized | 5428 | 0.4 | 230 | 499.376 | 922.3 | 460574.4848 | 60% | 276344.6909 | 184229.7939 | 24.51 | 4.1 | 75285.5053 | 9.5 | 4744.072 | 70541.4333 | 900 | 449438.4 | 6.3713 | 0.13096 | 60.3168
26 | Kassam Stadium | High | 3 | Sized | 5428 | 0.462 | 230 | 576.7793 | 922.3 | 531963.5299 | 80% | 425570.824 | 106392.706 | 24.51 | 4.1 | 108669.5099 | 7.6 | 4383.5225 | 104285.9874 | 700 | 403745.496 | 3.8715 | 0.13096 | 69.6659
13 | Holiday Inn | Low | 1 | Sized | 4424 | 0.294 | 230 | 299.1509 | 922.3 | 275906.8566 | 40% | 110362.7426 | 165544.114 | 24.51 | 3 | 32016.2316 | 11.4 | 3410.32 | 28605.9116 | 1100 | 329065.968 | 11.5034 | 0.13096 | 36.1328
13 | Holiday Inn | Central | 2 | Sized | 4424 | 0.4 | 230 | 407.008 | 922.3 | 375383.4784 | 60% | 225230.087 | 150153.3914 | 24.51 | 4.1 | 61360.1834 | 9.5 | 3866.576 | 57493.6074 | 900 | 366307.2 | 6.3713 | 0.13096 | 49.1602
13 | Holiday Inn | High | 3 | Sized | 4424 | 0.462 | 230 | 470.0942 | 922.3 | 433567.9176 | 80% | 346854.334 | 86713.5835 | 24.51 | 4.1 | 88569.2542 | 7.6 | 3572.7162 | 84996.538 | 700 | 329065.968 | 3.8715 | 0.13096 | 56.7801
24 | The Oxford Academy | Low | 1 | Sized | 9070 | 0.294 | 230 | 613.3134 | 922.3 | 565658.9488 | 40% | 226263.5795 | 339395.3693 | 24.51 | 3 | 65639.0644 | 11.4 | 6991.7728 | 58647.2917 | 1100 | 674644.74 | 11.5034 | 0.13096 | 74.0787
24 | The Oxford Academy | Central | 2 | Sized | 9070 | 0.4 | 230 | 834.44 | 922.3 | 769604.012 | 60% | 461762.4072 | 307841.6048 | 24.51 | 4.1 | 125799.4718 | 9.5 | 7927.18 | 117872.2918 | 900 | 750996 | 6.3713 | 0.13096 | 100.7873
24 | The Oxford Academy | High | 3 | Sized | 9070 | 0.462 | 230 | 963.7782 | 922.3 | 888892.6339 | 80% | 711114.1071 | 177778.5268 | 24.51 | 4.1 | 181582.9872 | 7.6 | 7324.7143 | 174258.2729 | 700 | 674644.74 | 3.8715 | 0.13096 | 116.4094
28 | Oxford Telephone Exchange | Low | 1 | Sized | 3900 | 0.294 | 230 | 263.718 | 922.3 | 243227.1114 | 40% | 97290.8446 | 145936.2668 | 24.51 | 3 | 28224.074 | 11.4 | 3006.3852 | 25217.6888 | 1100 | 290089.8 | 11.5034 | 0.13096 | 31.853
28 | Oxford Telephone Exchange | Central | 2 | Sized | 3900 | 0.4 | 230 | 358.8 | 922.3 | 330921.24 | 60% | 198552.744 | 132368.496 | 24.51 | 4.1 | 54092.3859 | 9.5 | 3408.6 | 50683.7859 | 900 | 322920 | 6.3713 | 0.13096 | 43.3374
28 | Oxford Telephone Exchange | High | 3 | Sized | 3900 | 0.462 | 230 | 414.414 | 922.3 | 382214.0322 | 80% | 305771.2258 | 76442.8064 | 24.51 | 4.1 | 78078.6825 | 7.6 | 3149.5464 | 74929.1361 | 700 | 290089.8 | 3.8715 | 0.13096 | 50.0547
5 | Oxford Business Park (OxBio Hub) | Low | 1 | Sized | 3243 | 0.294 | 230 | 219.2917 | 922.3 | 202252.698 | 40% | 80901.0792 | 121351.6188 | 24.51 | 3 | 23469.4031 | 11.4 | 2499.9249 | 20969.4782 | 1100 | 241220.826 | 11.5034 | 0.13096 | 26.487
5 | Oxford Business Park (OxBio Hub) | Central | 2 | Sized | 3243 | 0.4 | 230 | 298.356 | 922.3 | 275173.7388 | 60% | 165104.2433 | 110069.4955 | 24.51 | 4.1 | 44979.8993 | 9.5 | 2834.382 | 42145.5173 | 900 | 268520.4 | 6.3713 | 0.13096 | 36.0368
5 | Oxford Business Park (OxBio Hub) | High | 3 | Sized | 3243 | 0.462 | 230 | 344.6012 | 922.3 | 317825.6683 | 80% | 254260.5347 | 63565.1337 | 24.51 | 4.1 | 64925.4275 | 7.6 | 2618.969 | 62306.4586 | 700 | 241220.826 | 3.8715 | 0.13096 | 41.6224
7 | Oxford Business Park (John Wiley & Sons) | Low | 1 | Sized | 2784 | 0.294 | 230 | 188.2541 | 922.3 | 173626.738 | 40% | 69450.6952 | 104176.0428 | 24.51 | 3 | 20147.6467 | 11.4 | 2146.0965 | 18001.5502 | 1100 | 207079.488 | 11.5034 | 0.13096 | 22.7382
7 | Oxford Business Park (John Wiley & Sons) | Central | 2 | Sized | 2784 | 0.4 | 230 | 256.128 | 922.3 | 236226.8544 | 60% | 141736.1126 | 94490.7418 | 24.51 | 4.1 | 38613.6416 | 9.5 | 2433.216 | 36180.4256 | 900 | 230515.2 | 6.3713 | 0.13096 | 30.9363
7 | Oxford Business Park (John Wiley & Sons) | High | 3 | Sized | 2784 | 0.462 | 230 | 295.8278 | 922.3 | 272842.0168 | 80% | 218273.6135 | 54568.4034 | 24.51 | 4.1 | 55736.1672 | 7.6 | 2248.2916 | 53487.8756 | 700 | 207079.488 | 3.8715 | 0.13096 | 35.7314
21 | Wickes | Low | 1 | Sized | 2613 | 0.294 | 230 | 176.6911 | 922.3 | 162962.1646 | 40% | 65184.8659 | 97777.2988 | 24.51 | 3 | 18910.1296 | 11.4 | 2014.2781 | 16895.8515 | 1100 | 194360.166 | 11.5034 | 0.13096 | 21.3415
21 | Wickes | Central | 2 | Sized | 2613 | 0.4 | 230 | 240.396 | 922.3 | 221717.2308 | 60% | 133030.3385 | 88686.8923 | 24.51 | 4.1 | 36241.8985 | 9.5 | 2283.762 | 33958.1365 | 900 | 216356.4 | 6.3713 | 0.13096 | 29.0361
21 | Wickes | High | 3 | Sized | 2613 | 0.462 | 230 | 277.6574 | 922.3 | 256083.4016 | 80% | 204866.7213 | 51216.6803 | 24.51 | 4.1 | 52312.7173 | 7.6 | 2110.1961 | 50202.5212 | 700 | 194360.166 | 3.8715 | 0.13096 | 33.5367
30 | Storage King Oxford - Self Storage Units | Low | 1 | Sized | 3558 | 0.294 | 230 | 240.592 | 922.3 | 221897.9647 | 40% | 88759.1859 | 133138.7788 | 24.51 | 3 | 25749.0398 | 11.4 | 2742.7483 | 23006.2915 | 1100 | 264651.156 | 11.5034 | 0.13096 | 29.0598
30 | Storage King Oxford - Self Storage Units | Central | 2 | Sized | 3558 | 0.4 | 230 | 327.336 | 922.3 | 301901.9928 | 60% | 181141.1957 | 120760.7971 | 24.51 | 4.1 | 49348.8997 | 9.5 | 3109.692 | 46239.2077 | 900 | 294602.4 | 6.3713 | 0.13096 | 39.5371
30 | Storage King Oxford - Self Storage Units | High | 3 | Sized | 3558 | 0.462 | 230 | 378.0731 | 922.3 | 348696.8017 | 80% | 278957.4413 | 69739.3603 | 24.51 | 4.1 | 71231.7826 | 7.6 | 2873.3554 | 68358.4272 | 700 | 264651.156 | 3.8715 | 0.13096 | 45.6653
44 | Nuffield Trade and Industrial Park (Royal Mail East Oxford Delivery Office) | Low | 1 | Sized | 1897 | 0.294 | 230 | 128.2751 | 922.3 | 118308.1616 | 40% | 47323.2646 | 70984.897 | 24.51 | 3 | 13728.4791 | 11.4 | 1462.3366 | 12266.1425 | 1100 | 141102.654 | 11.5034 | 0.13096 | 15.4936
44 | Nuffield Trade and Industrial Park (Royal Mail East Oxford Delivery Office) | Central | 2 | Sized | 1897 | 0.4 | 230 | 174.524 | 922.3 | 160963.4852 | 60% | 96578.0911 | 64385.3941 | 24.51 | 4.1 | 26311.0913 | 9.5 | 1657.978 | 24653.1133 | 900 | 157071.6 | 6.3713 | 0.13096 | 21.0798
44 | Nuffield Trade and Industrial Park (Royal Mail East Oxford Delivery Office) | High | 3 | Sized | 1897 | 0.462 | 230 | 201.5752 | 922.3 | 185912.8254 | 80% | 148730.2603 | 37182.5651 | 24.51 | 4.1 | 37978.272 | 7.6 | 1531.9717 | 36446.3003 | 700 | 141102.654 | 3.8715 | 0.13096 | 24.3471
39 | Unicol Engineering | Low | 1 | Sized | 1652 | 0.294 | 230 | 111.7082 | 922.3 | 103028.5098 | 40% | 41211.4039 | 61817.1059 | 24.51 | 3 | 11955.4283 | 11.4 | 1273.4739 | 10681.9543 | 1100 | 122879.064 | 11.5034 | 0.13096 | 13.4926
39 | Unicol Engineering | Central | 2 | Sized | 1652 | 0.4 | 230 | 151.984 | 922.3 | 140174.8432 | 60% | 84104.9059 | 56069.9373 | 24.51 | 4.1 | 22912.9799 | 9.5 | 1443.848 | 21469.1319 | 900 | 136785.6 | 6.3713 | 0.13096 | 18.3573
39 | Unicol Engineering | High | 3 | Sized | 1652 | 0.462 | 230 | 175.5415 | 922.3 | 161901.9439 | 80% | 129521.5551 | 32380.3888 | 24.51 | 4.1 | 33073.3291 | 7.6 | 1334.1156 | 31739.2135 | 700 | 122879.064 | 3.8715 | 0.13096 | 21.2027
40 | Magdalen Centre (Sherrington Buidling) | Low | 1 | Sized | 2351 | 0.294 | 230 | 158.9746 | 922.3 | 146622.292 | 40% | 58648.9168 | 87973.3752 | 24.51 | 3 | 17014.0508 | 11.4 | 1812.3107 | 15201.7401 | 1100 | 174872.082 | 11.5034 | 0.13096 | 19.2017
40 | Magdalen Centre (Sherrington Buidling) | Central | 2 | Sized | 2351 | 0.4 | 230 | 216.292 | 922.3 | 199486.1116 | 60% | 119691.667 | 79794.4446 | 24.51 | 4.1 | 32607.9998 | 9.5 | 2054.774 | 30553.2258 | 900 | 194662.8 | 6.3713 | 0.13096 | 26.1247
40 | Magdalen Centre (Sherrington Buidling) | High | 3 | Sized | 2351 | 0.462 | 230 | 249.8173 | 922.3 | 230406.4589 | 80% | 184325.1671 | 46081.2918 | 24.51 | 4.1 | 47067.4314 | 7.6 | 1898.6112 | 45168.8202 | 700 | 174872.082 | 3.8715 | 0.13096 | 30.174
22 | Sandhills Community Primary School | Low | 1 | Sized | 2542 | 0.294 | 230 | 171.89 | 922.3 | 158534.1839 | 40% | 63413.6736 | 95120.5103 | 24.51 | 3 | 18396.3067 | 11.4 | 1959.5465 | 16436.7602 | 1100 | 189079.044 | 11.5034 | 0.13096 | 20.7616
22 | Sandhills Community Primary School | Central | 2 | Sized | 2542 | 0.4 | 230 | 233.864 | 922.3 | 215692.7672 | 60% | 129415.6603 | 86277.1069 | 24.51 | 4.1 | 35257.1397 | 9.5 | 2221.708 | 33035.4317 | 900 | 210477.6 | 6.3713 | 0.13096 | 28.2471
22 | Sandhills Community Primary School | High | 3 | Sized | 2542 | 0.462 | 230 | 270.1129 | 922.3 | 249125.1461 | 80% | 199300.1169 | 49825.0292 | 24.51 | 4.1 | 50891.2848 | 7.6 | 2052.8582 | 48838.4267 | 700 | 189079.044 | 3.8715 | 0.13096 | 32.6254
99 | Oxford Retail Park (TESCO SUPERSTORE) | Low | 1 | Sized | 6954 | 0.294 | 230 | 470.2295 | 922.3 | 433692.6494 | 40% | 173477.0598 | 260215.5896 | 24.51 | 3 | 50325.695 | 11.4 | 5360.6161 | 44965.079 | 1100 | 517252.428 | 11.5034 | 0.13096 | 56.7964
99 | Oxford Retail Park (TESCO SUPERSTORE) | Central | 2 | Sized | 6954 | 0.4 | 230 | 639.768 | 922.3 | 590058.0264 | 60% | 354034.8158 | 236023.2106 | 24.51 | 4.1 | 96450.885 | 9.5 | 6077.796 | 90373.089 | 900 | 575791.2 | 6.3713 | 0.13096 | 77.274
99 | Oxford Retail Park (TESCO SUPERSTORE) | High | 3 | Sized | 6954 | 0.462 | 230 | 738.932 | 922.3 | 681517.0205 | 80% | 545213.6164 | 136303.4041 | 24.51 | 4.1 | 139220.2969 | 7.6 | 5615.8835 | 133604.4134 | 700 | 517252.428 | 3.8715 | 0.13096 | 89.2515
103 | Oxford University Press | Low | 1 | Sized | 4584 | 0.294 | 230 | 309.9701 | 922.3 | 285885.4048 | 40% | 114354.1619 | 171531.2429 | 24.51 | 3 | 33174.1424 | 11.4 | 3533.6589 | 29640.4835 | 1100 | 340967.088 | 11.5034 | 0.13096 | 37.4396
103 | Oxford University Press | Central | 2 | Sized | 4584 | 0.4 | 230 | 421.728 | 922.3 | 388959.7344 | 60% | 233375.8406 | 155583.8938 | 24.51 | 4.1 | 63579.3582 | 9.5 | 4006.416 | 59572.9422 | 900 | 379555.2 | 6.3713 | 0.13096 | 50.9382
103 | Oxford University Press | High | 3 | Sized | 4584 | 0.462 | 230 | 487.0958 | 922.3 | 449248.4932 | 80% | 359398.7946 | 89849.6986 | 24.51 | 4.1 | 91772.4822 | 7.6 | 3701.9284 | 88070.5538 | 700 | 340967.088 | 3.8715 | 0.13096 | 58.8336
61 | Leonardo Royal Hotel Oxford | Low | 1 | Sized | 7218 | 0.294 | 230 | 488.0812 | 922.3 | 450157.2539 | 40% | 180062.9015 | 270094.3523 | 24.51 | 3 | 52236.2477 | 11.4 | 5564.1252 | 46672.1225 | 1100 | 536889.276 | 11.5034 | 0.13096 | 58.9526
61 | Leonardo Royal Hotel Oxford | Central | 2 | Sized | 7218 | 0.4 | 230 | 664.056 | 922.3 | 612458.8488 | 60% | 367475.3093 | 244983.5395 | 24.51 | 4.1 | 100112.5234 | 9.5 | 6308.532 | 93803.9914 | 900 | 597650.4 | 6.3713 | 0.13096 | 80.2076
61 | Leonardo Royal Hotel Oxford | High | 3 | Sized | 7218 | 0.462 | 230 | 766.9847 | 922.3 | 707389.9704 | 80% | 565911.9763 | 141477.9941 | 24.51 | 4.1 | 144505.6231 | 7.6 | 5829.0836 | 138676.5396 | 700 | 536889.276 | 3.8715 | 0.13096 | 92.6398
52 | The Manor Hospital | Low | 1 | Sized | 4354 | 0.294 | 230 | 294.4175 | 922.3 | 271541.2418 | 40% | 108616.4967 | 162924.7451 | 24.51 | 3 | 31509.6457 | 11.4 | 3356.3593 | 28153.2864 | 1100 | 323859.228 | 11.5034 | 0.13096 | 35.561
52 | The Manor Hospital | Central | 2 | Sized | 4354 | 0.4 | 230 | 400.568 | 922.3 | 369443.8664 | 60% | 221666.3198 | 147777.5466 | 24.51 | 4.1 | 60389.2944 | 9.5 | 3805.396 | 56583.8984 | 900 | 360511.2 | 6.3713 | 0.13096 | 48.3824
52 | The Manor Hospital | High | 3 | Sized | 4354 | 0.462 | 230 | 462.656 | 922.3 | 426707.6657 | 80% | 341366.1326 | 85341.5331 | 24.51 | 4.1 | 87167.8419 | 7.6 | 3516.1859 | 83651.656 | 700 | 323859.228 | 3.8715 | 0.13096 | 55.8816